Annex 4 Goods and services specification

For the supply of Access control system and Security check point for British Council

| SN | Description | Unit | Quantity |
| --- | --- | --- | --- |
| A | Access control system |  |  |
| 1 | Supply, Installation, Testing & Commissioning of Surface mount wiegand card reader with keypad capable of reading card format of 125kHz EM, IK10 rated, IP67 or above, complete as required Make: BOSCH or Equivalent | Pcs | 7.00 |
| 2 | Supply, Installation, Testing & Commissioning of DIN rail mount 4 door access controller upto 4 wiegand reader support Latest integrated 32-bit, 30 Mhz Micro-controller based system architecture; on board real time clock access controller shall have 8 Relay outputs; 8 Analog Inputs; onboard LCD display 16 Characters 16-characters liquid crystal display (LCD), with Power supply, Maintenance free 7 Amp battery, and vendal resistant metal enclosure with lockable key and tempar feature and complete accessories as per the specification. Make: BOSCH or Equivalent | Pcs | 2.00 |
| 3 | Supply, Installation, Testing & Commissioning of Door contact with NO/NC features (i.e. triggered while state change from NC to NO or NO to NC) min range of 5mm. Make: BOSCH or Equivalent | Pcs | 7.00 |
| 4 | Supply, Installation, Testing & Commissioning of Single leaf Electro Magnetic lock capacity of (Min 600 lbs) with LED & and Z/L brackets to make the system complete. | Pcs | 3.00 |
| 5 | Supply, Installation, Testing & Commissioning of Release buttons with Exit Sign Printed (in steel plate) complete as required. | Pcs | 3.00 |
| 6 | Supply, Installation, Testing & Commissioning of Emergency door release button complete as required. | Pcs | 7.00 |
| 7 | Integration of the above system with the existing fire alarm system using the fire relay module as required. | Job | 1.00 |
| 8 | Supply, Installation, Testing & Commissioning of Access Control Software: The Access Control System shall have a multi-level priority interrupt structure proven in multi-tasking and multi-client real time applications. Simultaneous alarms/events monitoring by multiple users, system supervision and history archiving shall be possible without degradation of any functionality specified for system or operation. The Access Control System server shall act as the source that provides time synchronization across all sub-systems. The system shall be a flexible and user-friendly workstation providing user(s) with a Graphical User Interfaces (GUIs) for alarm monitoring and control that includes map viewer with alarm list and a swipe ticker for visual door monitoring. The system shall contain a map viewer. This map viewer shall provide a graphical presentation of the premises by means of floor plans, pictures or any desired graphical representation. The Access Control System shall provide a web based import and export interface to import cardholder master records from a separate database during installation, or to export the master records for further use by another application in CSV format. The access control system shall provide a real time swipe ticker such as; The name of the cardholder and their stored photo, for visual confirmation of identity., A time stamp., Company and/or department name., The entrance and the reader at which the credential was used An event category: Green- Access event, Yellow- Incomplete access, Red- Invalid access. The Access Control System AS shall provide a wide range of standard events such as, unknown card, unauthorized card, Outside time profile, Card anti-pass back, Access timeout, Door opened unauthorized, Door blocked, Tamper alarm controller, Tamper alarm reader, PIN code error, Access denied, Wrong card version, Card blocked, Card blacklisted etc.. The Access Control System shall be capable to support to the following with additional expansion licenses if required: • Number of active cardholders – 400,000 • Number of readers – 10,000 • Number of access groups – 255 • Number of time schedules – 255 • 4 – 8 digits programmable (Personal Identification Number) PIN codes • Map viewer floor plans – 1,000 Make: BOSCH or Equivalent | Set | 1.00 |
| 9 | Supply and installation of 8 C x 1.0 Sq mm, multistranded DC shielded Reader Cable complete as required. | Rmtr | 500.00 |
| 10 | Supply and installation of 4 C x 1.0 Sq mm, multistranded DC shielded Cable complete as required. | Rmtr | 500.00 |
| 11 | Supply and installation of 2 C x 1.0 Sq mm, multistranded DC shielded Cable complete as required. | Rmtr | 160.00 |
| 12 | Supply and installation of FRLS 20MM Conduit | Rmtr | 500.00 |
| B | Security check point |  |  |
| 1 | Supply, Installation, Testing & Commissioning of 32 zone door frame metal detector with required accessories. Make: GARRETT,SMITHs or Equivalent | Set | 1 |